SPRINT 2 PROGRESS REPORT

CeDInt-SEF DataPack · Storey 1 energy-waste finder · TBDA Group 1

Sprint Review, 26 October 2026 · Sprint 1: 28 Sep – 11 Oct · Sprint 2: 12 – 25 Oct · status of Jira on 25 Oct

1. Summary

Product goal: help CeDInt find, value and act on avoidable electricity use on Storey 1, first on historical data and ready to run on the live IoT platform.

Where we are: the data foundation is complete. The four zone files are combined, cleaned, converted to Madrid time and enriched with weather, the UPM calendar and hourly electricity prices. On that dataset we made a first estimate of the waste, a business case, a first forecasting baseline and the dashboard skeleton.

First result: most of the waste comes from plug circuits in zone NW that stay on at night, at weekends and during holidays, most likely heaters left on in empty rooms.

| 59 % of non-essential electricity used while the building is closed | 5.5 – 7.9 MWh out-of-hours waste per year on Storey 1 | € 790 – 1,130 cost of that waste per year | 0.55 – 0.79 t CO₂ per year |
| --- | --- | --- | --- |

Estimates on 2021–22 data, valued at € 0.142/kWh (Eurostat, all-in) and 0.10 kg CO₂/kWh (temporary, until the CO₂ data arrive.

2. How we work: Scrum after your feedback

We rebuilt the Product Backlog following your feedback and the course notes on Scrum:

- Stakeholder features, not tasks

- Ordered by value, sprint-agnostic.

- Jira is the sprint backlog

- Estimates by the Development Team.

- 3. What we delivered

| AREA | DELIVERED | JIRA | STATUS |
| --- | --- | --- | --- |
| Data foundation | Four zone files combined into one dataset (loader, unified columns, Parquet) | KAN-11 | Done |
| Data foundation | Data reliability report: every column rated (18 reliable, 6 with caution, 4 unreliable, 2 excluded), gaps, duplicates, level shifts and impossible values, with the rules applied | KAN-12 | Done |
| Data foundation | Cleaning of counter resets, outliers and negative values, with documented rules | KAN-13 | Done |
| Data foundation | Timezone fixed: UTC converted to Madrid time, daylight-saving days checked | KAN-122 | Done |
| Data foundation | Clean hourly dataset (kWh per zone and load type) | KAN-123 | Done |
| External data | Hourly Madrid weather | KAN-14 | Done |
| External data | Holiday and UPM academic calendar (incl. Christmas, Holy Week, August closure, lockdown) | KAN-125 | Done |
| External data | Hourly electricity market prices (OMIE); CO₂ factor waiting for an external institution | KAN-134 | Waiting |
| Stakeholders | Stakeholder map at strategic, tactical and operational level; personas with needs, pains and focus metrics; KPIs the client wants to see | KAN-120, KAN-41 | Done |
| Scrum | Product Backlog rebuilt after your feedback | – | Done |
| Forecasting | Average-profile baseline (hour × weekday) built and evaluated | KAN-72, KAN-73 | Done |
| Forecasting | First model for NW plugs: linear regression with weather, calendar and past use, compared with two baselines on a time-based split | KAN-20 | In progress |
| Business value | Business question, definition of waste and business case with first € / CO₂ estimate, | , KAN-132 | In progress |
| Business value | Method for € and CO₂ per alert and Low / Medium / High severity, tested | KAN-23, KAN-152 | In progress |
| Business value | Deployment plan for live data (first version) | KAN-159 | In progress |
| Dashboard | Streamlit skeleton that runs with one command, ready for review (pull request #5) | KAN-118 | In progress |
| Dashboard | Low-fidelity wireframe of all screens | KAN-121 | In progress |

4. What the data tell us

- Two data periods. Hourly data from April 2020 to February 2023, then minute data from August to October 2025, with a 901-day hole in between. There are no duplicates. All four zones together have a valid value in 78.6 % of the hours. Models are trained on 2020–23; 2025 is kept for testing and the demo.

- Data reliability. Of 30 measurement columns, 18 are reliable, 6 need caution, 4 are unreliable and 2 are excluded. Examples: NW emergency lighting reads negative 97.7 % of the time (probably a reversed meter), SE emergency lighting and HVAC read zero together for about 2,100 hours, the presence sensors are stuck at 1.0 for weeks in NW and SE, the SE projector is always zero and the SW server rack stops on 3 December 2021.

- High base load. 59 % of the non-essential electricity is used while the building is closed. Plug circuits are 77 % of the non-essential energy and about 70 % of the waste.

- Winter pattern in NW. NW plug consumption at night is 2.8 times higher in winter than in summer (1.4 kW vs 0.5 kW), and the largest out-of-hours periods are winter weekends and the Christmas break.

- Focus pays off. With our severity levels, about 4 High alerts a week cover 73 % of the money at stake: a workload one person can handle.

- First forecast. For NW plugs, a linear regression with outdoor temperature, calendar and past use misses by 202 W on average in the validation period (May–Oct 2022), with an error of 51 % of average use, against 67–81 % for the simple baselines (R² on the training data: 0.58). Consumption rises as it gets colder, which supports the heating finding. The ASHRAE Guideline 14 target is 30 %, so the next step is the LightGBM model.

5. Next steps: priorities for Sprint 3 (26 Oct – 8 Nov)

Our proposal for the Sprint 3 Planning, in order of priority. The final selection will be made this week.

| # | PRIORITY | WHY | STORY |
| --- | --- | --- | --- |
| 1 | Review and merge the dashboard skeleton (pull request #5), then build the overview and out-of-hours pages | Gives the building manager the first usable screen; every later page builds on it | F1.1, F1.2 |
| 2 | Detect out-of-hours waste with the standby-baseline rule | Core of the product; the alert list, € and CO₂, severity and the measured business case all depend on it | F4.1 |
| 3 | Expected consumption: baselines on the clean data and the actual-vs-expected chart | Defines "normal" and sets the accuracy bar the ML model must beat | F3.1 |
| 4 | Weather- and calendar-aware model (LightGBM) with time-based evaluation | Fewer false alarms on cold days and in exam periods | F3.2 |
| 5 | One alert table for all detectors, valued in € and CO₂ with the real hourly prices | Single source for the alert list, floor map and savings report | F4.2, F5.1 |
| 6 | Business case updated with the measured waste | Replaces the estimate with what the detector actually finds | F6.1 |
| 7 | Data dictionary, experiment log and docs site | Makes every number reproducible and auditable (quality requirement Q1) | Q1 |